## BoM- Burla MTL
Schedule of Items
Sl. No. | Description | Unit | Quantity | Spare Quantity | Total Quantity | Unit Price (Rs.) | GST (Rs.) | Unit Price - All Inclusive (Rs.) | Total Amount (All Inclusive) (Rs.)
A | SUPPLY OF MATERIAL
A1 | Supply of UPS with Battery Bank - Supply part
1 | Supply of UPS 20kVA-3Phase In/3Phase Out online UPS with (3Ph+N+E) (As per Ts) | Nos | 2 | 0 | 2
2 | Supply of Battery Bank with connectors & accessories
2.1 | SMF VRLA Battery Bank with 12V, capacity 120AH along with connectors & accessories | Nos | 40 | 0 | 40
3 | Microprocessor based MCCB
3.1 | Incomer Microprocessor Based MCCB (Single input single output/4P-63Amps) | Nos | 2 | 0 | 2
4 | Cables required for connections
4.1 | Cables from ACDB to UPS-1.1kV armoured XLPE cable 4C*16 sqmm Cu cable | metre | 50 | 0 | 50
4.2 | Cables from UPS to Battery Bank- 1.1kV armoured XLPE cable 4C*16 sqmm Cu cable | metre | 50 | 0 | 50
4.3 | Cables from UPS to changeover switch- 1.1kV armoured XLPE cable 4C*16 sqmm Cu cable | metre | 50 | 0 | 50
4.4 | Cables from Battery to UPS- 1.1kV armoured XLPE cable 4C*16 sqmm Cu cable | metre | 50 | 0 | 50
4.5 | Cables for Earthing 1.1kV LT 1C*10 sqmm Cu power cable | metre | 20 | 0 | 20
5 | Earthing
5.1 | Earthing for changeover switch & others | Nos | 6 | 0 | 6
6 | Microprocessor based MCCB for Changeover switch
6.1 | Microprocessor Based MCCB (Double input single output/4P-63Amps) | Nos | 2 | 0 | 2
7 | Bypass SCVS in bypass path of standalone UPS | Nos | 1 | 0 | 1
8 | Bypass Isolation Transformer | Nos | 1 | 0 | 1
Total Cost for the Project

## Sheet5
Sl. No. | Item | Prefered Make
1 | Supply of UPS 20kVA-3Phase In/3Phase Out online UPS with (3Ph+N+E) | Eaton,APC, Delta,Vertiv,Legrand(Numeric India)
2 | SMF VRLA Battery Bank with 12V, capacity 120AH along with connectors & accessories | Exide, Amaron,HBL
3 | Incomer Microprocessor Based MCCB (Single input single output/4P-63Amps) | ABB,Siemens L&T, Schneider
4 | 1.1kV LT Power Cable | Havells, KEI, Polycab, Dynamic,Gemscab
5 | Microprocessor Based MCCB (Double input single output/4P-63Amps) | ABB,Siemens L&T, Schneider

## BoM- Rajgangpur & Balangir MTL
Schedule of Items
Sl. No. | Description | Unit | Quantity | Spare Quantity | Total Quantity | Unit Price (Rs.) | GST (Rs.) | Unit Price - All Inclusive (Rs.) | Total Amount (All Inclusive) (Rs.)
A | SUPPLY OF MATERIAL
A1 | Supply of UPS with Battery Bank - Supply part
1 | Supply of UPS 20kVA | Nos | 1 | 0 | 1
1.1 | 3Phase In/3Phase Out online UPS with (3Ph+N+E) (As per Ts)
2 | Supply of Battery Bank with connectors & accessories
2.1 | SMF VRLA Battery Bank with 12V, capacity 120AH along with connectors & accessories | Nos | 20 | 0 | 20
3 | Microprocessor based MCCB
3.1 | Incomer Microprocessor Based MCCB (Single input single output/4P-63Amps) | Nos | 1 | 0 | 1
4 | Cables required for connections
4.1 | Cables from ACDB to UPS-1.1kV armoured XLPE cable 4C*10 sqmm Cu cable | metre | 25 | 0 | 25
4.2 | Cables from UPS to Battery Bank- 1.1kV armoured XLPE cable 4C*10 sqmm Cu cable | metre | 25 | 0 | 25
4.3 | Cables from UPS to changeover switch- 1.1kV armoured XLPE cable 4C*10 sqmm Cu cable | metre | 25 | 0 | 25
4.4 | Cables from Battery to UPS- 1.1kV armoured XLPE cable 4C*10 sqmm Cu cable | metre | 25 | 0 | 25
4.5 | Cables for Earthing 1C*10 sqmm Cu Cable | metre | 20 | 0 | 20
5 | Earthing
5.1 | Earthing for changeover switch & others | Nos | 6 | 0 | 6
6 | Microprocessor based MCCB for Changeover switch
6.1 | Microprocessor Based MCCB (Double input single output/4P-63Amps) | Nos | 1 | 0 | 1
7 | Bypass SCVS in bypass path of standalone UPS | Nos | 1 | 0 | 1
8 | Bypass Isolation Transformer | Nos | 1 | 0 | 1
Total Cost for the Project

## Burla SLD
Main Supply
From → To | Service | Proposed Cable | Est. Ampacity* | Remarks
UPS‑1 → MCCB‑1 | Incomer | 4C × 16 mm² Cu, XLPE, armoured | ~45–55 A | In tray; confirm derating for grouping/ambient.
UPS‑2 → MCCB‑2 | Incomer | 4C × 16 mm² Cu, XLPE, armoured | ~45–55 A | Same as above.
Changeover Switch → CB‑3 (Outgoing) | Outgoing | 4C × 16 mm² Cu, XLPE, armoured | ~45–55 A | Increase to 16 mm² Cu if long run or high VD.
Earthing (each source & outgoing) | PE | 1 × 10 mm² Cu (green‑yellow) | — | Separate Earthing to earth flat
UPS 1 -
20 kVA
UPS 2 -
20 kVA
Incomer Microprocessor Based MCCB 1
(4P-63Amps)
Double Input and Single Output Mannual Changeover Microprocessor based MCCB
(4P-63Amps)
Connected Load
Battery Bank
40 Nos.
12V, 120AH
Incomer Microprocessor Based MCCB 2
(4P-63Amps)
Bypass Stabilizer
Bypass Isolation Transformer
Similar Old Existing System
ACDB
Double Input and Single Output Mannual Changeover Microprocessor based MCCB
(4P-63Amps)

## Rajgangpur & Balangir
Main Supply
Old UPS 1-
20 kVA
New UPS -
20 kVA
Incomer Microprocessor Based MCCB 1
(4P-63Amps)
New Battery Bank
20 Nos.
12V, 120AH
Incomer Microprocessor Based MCCB 2
(4P-63Amps)
Bypass Stabilizer
Bypass Isolation Transformer
Connected Load
ACDB
Double Input and Single Output Mannual Changeover Microprocessor based MCCB
(4P-63Amps)