## Motorized AB switch
SL.NO. | TECHNICAL PARTICULARS | DESIRED VALUE
1 | Rating of AB Switch | 400 Amps AB Switch | 200 Amps AB Switch
1.a | Reference standards (latest amend.) | IS 9920, IEC 129, IEC 62231,IS 1239
2 | Installation | Outdoor
3 | Suitable for Mounting | Horizontal Rotating Type
4 | Type | 3 Pole | 3 Pole
5 | Service Voltage | 11 kV | 11 kV
6 | Rated Voltage | 12 kV | 12 kV
7 | Rated Frequency | 50 Hz | 50 Hz
8 | Continuous current rating at | 400 Amps | 200 Amps
design ambient temp of 50
Deg C
9 | Rated short time current | 16 kA for 1sec | 16 kA for 1sec
10 | Rated peak withstand current | 40 kA | 40 kA
11 | Rated main active load breaking capacity | 10 Amp | 10 Amp
12 | Rated line charging breaking capacity | 2.5A | 2.5A
12.a | Rated Cable charging breaking capacity | 10A | 10A
13 | Rated Transformer off load breaking Capacity | 6.3A | 6.3A
14 | One minute power frequency with stand voltage Dry | 35kV RMS | 35kV RMS
15 | One minute power frequency withstand voltage Wet | 35kV RMS | 35kV RMS
16 | Dry flashover Voltage | 55kV | 55kV
17 | Power Frequency puncture withstand voltage | 1.3 times of actual dry flashover Voltage
18 | Visible Discharge Voltage | 9kV RMS
19 | 1 Minute Power Frequency withstand voltage between pole and earth | 28kV RMS | 28kV RMS
20 | 1 Minute Power frequency withstand voltage across the isolation distance | 32kV RMS | 32kV RMS
21 | Impulse with stand voltage for positive and negative polarity (1.2 / 50) micro second wave)
a | Across Isolating distance | 85kV Peak | 85kV Peak
b | To earth and between poles | 75kV Peak | 75kV Peak
22 | No. of Post Per Pole (Polymeric, IEC 62231) | 2 | 2
23 | Total No. of post for 3 phases | 6 | 6
24 | Minimum Creepage Distance | 31 mm/kV | 31 mm/kV
25 | System Neutral Earthing | Effectively Earthed | Effectively Earthed
27 | Operating mechanism | Motorized and Manual | Motorized and Manual
28 | Operating Time | <=12 sec | <=12 sec
SL. | TECHNICAL PARTICULARS | DESIRED VALUE
NO.
29.a | FRP Dia. of the Post Insulator (min.) | 24mm | 24mm
29.b | Dai of Weather sheds | >100mm | >100mm
29.c | Thickness of Housing (min) | 3mm | 3mm
29.d | Type of Sheds | Aerodynamic | Aerodynamic
30 | Phase to Phase Clearance | 760mm | 760mm
31 | Isolation Distance in switch open condition | 380mm | 380 mm
32 | Vertical clearance from Top of Insulator cap to mounting channel | 254mm (min) | 254mm (min)
33 | Copper contacts Temp in Air should not exceed | 65Degree | 65 Degree
| Size of fixed contacts (Copper Type Electrolytic with silver plated) | 80mmx50mmx8mm (50x8x2 Fingers) | 70mmx35mmx6mm (35x6x2 Finger)
34 | (coating thickness not less than 10 microns)
Size of Moving contacts (Copper Type Electrolytic with silver plated) (coating thickness not less than 10
35 | microns) | 220mmx50mmx8mm | 220mmx35mmx6mm
36 | Moving Contact supporting Angle | 50mmx50mmx5mm | 45mmx45mmx5mm
37 | Size of rods used for arcing horns | 10 mm | 8 mm
38 | Insulation for tinned Copper braid/rope | Polyolefin, (RSFR-H) type | Polyolefin, (RSFR-H) type
39 | Copper Flexible BRAIDED Tape - 320mm Long, Tined plated with | 450gm /Mtr | 450gm /Mtr
Brass Nut, bolt & Washers
| Minimum size*Length of Coupling Hot Dip GI Solid Pipe for Phase | 25mm Dia &1800 mm long | 25mm Dia &1800mm long
40 | coupling pipe, B Class ( Nominal Bore)
41 | Operating Down Pipe, B class (IS 1239) (Nominal bore) | 32mm Dia & 7Mtr Long (one piece) | 32mm Dia & 7Mtr Long (one piece)
Temperature Rise Limit (w.r.t ambient temp)
42 | - Tinned Copper contacts | 65°C | 65°C
| - Terminals | 65°C | 65°C
| - Metal Parts | 40°C | 40°C
43 | Bearings | 4 nos. self-lubricating bearing to be provided with grease nipple including 4th bearing being a thrust bearing.
44 | Locking arrangement | Provision for pad locking at both ‘ON’ & ‘OFF’ Position
45 | Earth Terminal | M12 Bolts with nuts and flat washer shall be provided at base channel as earthing Terminal.
46 | ‘T’ Connection | The T connection provided on the channel having ‘moving contact’ shall be G.I Nut & bolt at the bottom end to facilitate replacement of this unit only during requirements & avoid entire change of arm.
47 | ‘I’ bolt | The I bolt shall be longer with 75 mm thread.
48 | Mounting Channel HDG 100 microns | 75x40x4.8 mm hot dip galvanized channel length 480 mm min. (C/C slotted hole 18x 36 mm- 250mm)
49 | Connectors | Connectors shall be of hard drawn electrolytic copper or brass. The connector should be of 4 bolted type and suitable for 55- 148 sqmm AAAC conductor.Or SOCKET: Two no. of bimetallic copper sockets shall be used at both ends suitable for 55-148 sqmm AAAC conductor.
50 | Marking/Engraving (Parameters should be embossed on SS sheet of thickness 1mm with black background.It should be riveted on MS channel of AB switch) | 1. Rated Voltage
2. Manufacturer Name
3. Month/Year of Manufacture
4. Serial No.
5. PO No.
6. Rated Normal Current in Amps
7. Rated One Second Short-Time Current
51 | Pressure Spring | Stainless steel

## FPI with Accessories
Sr. No. | Technical requirement | TPWODL Requirement | BIDDER RESPONSE
A | For Communicable FPI
1 | Offered Model no. or type of FPI for Overhead lines along with Make | Bidder to submit followings, a. Make- Electrolyte/ Sugslloyd / Megger b. Model no./Type c. Country of origin
2 | Application | Product shall be suitable for application on overhead lines of different size conductors and ABC
3 | Power | Self- powered for normal functioning without external auxiliary power for FPI
3 | Supply voltage Suitability | Suitable for 7 KV to 33 KV overhead conductors
4 | Power Frequency | 50Hz
5 | Ingress Protection of enclosure | IP67 or better
6 | Short - circuit withstand | 25kA/170 ms
7 | Suitable diameter of jaw | Suitable for Conductor- Dog, Wolf, Panther, Goat, Zebra
8 | Conformal coating | The relay PCB should have conformal coating.
Fault Detection Parameters
9 | Current setting Trigger value | 100 A to 800 A steps of 100 A and Manually or Automatic Mode- Can be set on site remotely
10 | Transient faults detection feature | This feature can be made On or Off, Manually and Remotely as per application site need.
11 | Minimum fault current impulse filter time | 60 to 300ms (To filter inrush current)
12 | Beacon Flash Indication Duration (user settable) | 30 min to 720 min in steps of 30 min - Manual and Remote Settable
13 | Inrush transient restraint | 2 sec
Reset (Permanent Fault)
14 | Auto-reset on restoration on supply | Should auto-reset after 30 seconds delay and within one min of supply restoration.
15 | Pre-set Timer Reset | 30 min to 360 min in steps of 30 min - Manual and Remote Settable
16 | Manual Reset (Local and Remote both) | Manual and Remote Resettable
Fault indication
17 | Fault Indications | Bright Red flash light (LEDs) for permanent faults, Preferably Green LED for transient fault with different blinking rate Preferably Yellow LED for low battery indication Bidder to submit the offered equipment details of features for indication of above faults categories.
18 | Light Power | 40 Lumens
19 | Visibility Angle | 360 Degree and 300 mtr
20 | Flash Period for permanent faults | 1 flash every 3 sec and/or Red flashing LED
21 | Flash Period for transient faults | 2 flash every 12 sec and/ or Green flashing LED
22 | Standard total flash duration | Min. 1000 Hrs under permanent fault operation
23 | Battery low indication | The FPI should have low battery indication Local and remote alert (Bidder to submit details of provision)
24 | Internal Battery of FPI | Lithium Ion rechargeable battery (Shall recharge from line current)
25 | Life of the Battery (In operating condition) | More than 10 years
26 | Shelf Life of battery | More than 15 years
27 | FPI Battery capacity | Bidder to mentioned details of voltage and Ah rating
28 | Operation Temperature | -5 deg. C to +70 deg. C or better
29 | Storage Temperature | -5dec. C to +70 deg. C or better
30 | Suitability for Wind Resistance | For wind pressure 200kg/sqm up to an elevation of 10 mts
31 | Weight of FPI unit | Bidder to submit details of offered product
32 | Size of FPI unit (Dimensions) | Bidder to submit details of offered product
33 | Fixing on line conductor | Should be Easy to fix with hot stick
34 | FPI power up current | FPI should be power up with Minimum 5A line current & battery power shall be used only after fault
35 | Data Transmission/collector Unit package | This package shall include, Data Collector or Communication unit Battery bank Resin cast PT for auxiliary supply. 4G Modem/RTU for SCADA communication Communication cables and supply cables Installation hardware with GI material for all equipment (Bidder to mention the package details along with Make and model of equipment)
36 | Inbuilt Radio range | 100 meter (A short-range radio interface shall be embedded in this Fault Passage Indicator/ so that to allow it communicate with the 2G/3G/4G/ 4G LTE, etc. communication interface)
37 | Communication Unit devise interface | A GSM/GPRS communication interface, pole-mounted, acting as a communication gateway between Fault Passage Indicators using short-range radio and the remote control center using GSM/GPRS communication. Inbuilt modem shall support all technology i.e. 2G, 3G, 4G & 4G LTE, 5G etc.
38 | SMS Alert | SMS alarm forwarding facility available for at least 5 different numbers.
39 | Communicable protocol for future support | Communicable protocol like IEC 101 & 104 & MQTT should be provided for future support.
40 | The communication unit protocol with server | The communication unit should provide data to SCADA in IEC-60870-5-104 and MQTT over the Ethernet port.
41 | Line Loading data | FPI should transmit real time line loading (phase wise), fault data to ADMS through FPI over IEC-60870-104 and MQTT.
42 | The DCU communication compatibility | Compatible to send data over 2G/3G/4G/RF modem connected to the Ethernet port of the modem
43 | Data Transmission rate | Data Transmission rate over Ethernet should be 10/100Mbps
44 | Multi master reporting | One DCU (if required)/FPI should report at- least 8 master with single CASDU
45 | FPI Data downloading at site | Data downloading from FPI to Laptop should be possible over any non- proprietary protocol. LAPTOP software to be provided free of cost & should be compatible with windows 10 and latest edition
46 | Self-diagnostic alerts in DCU | DCU Door open alarm, Battery charger failure, LT Supply failure, Battery low alarm, DCU Malfunction
47 | Communication unit battery back up | Battery (Along with charger) backup of 4 hrs. Should be provided for automation unit. Aux PT should be Ph-Ph. Aux Supply VDC 24 or higher
48 | Installation supervision | The bidder shall provide installation supervision
49 | SCADA integration of data. | The scope shall include the data integration up to SCADA.
50 | DCU and Modem | Remote Configuration should be compatible
51 | For Modem (4G) | Provision required for Automatic restart (configurable)
4.1 CONTROLLER FOR FPI
Sr. No. | Technical requirement | TPWODL Requirement | BIDDER RESPONSE
1 | Make & Model Proposed | Make
Model
2 | Controller Redundancy | Optional (CPU, Power, Communication & Memory)
3 | Digital Inputs (Wireless) | As per RFP / FPI type and Indicative Signal List
4 | Digital Outputs (Wireless) | As per RFP / FPI type and Indicative Signal List
5 | Analog Inputs (Wireless) | As per RFP / FPI type and Indicative Signal List
6 | FPI Integration (Wireless) | Facility to interface FPI through high frequency wireless module. (Fault Passage Indicator should have a short-range radio interface embedded in it to communicate with DCU) Capable of Acquiring 32 bit Analog and Accumulator Data from nearby (100 meter) 9 nos. FPIs (3X 3 sets) without any additional license/ hardware enhancement
7 | CPU Processing Speed | 32 bit ARM Core CPU operating @ minimum 450 MHz
8 | Ports Requirement and Type For Structuring (Configuration) System (Separate Port) | All ports shall be galvanically isolated
2 Nos. Ethernet Ports / FRTU ( Both the ports should support IEC 104 other standard protocols for Communication with MODEM )
A galvanically isolated USB port for local engineering through laptop
9 | Protocol Support | IEC60870-5-104 (Master & Slave), MODBUS (Serial & TCP/IP), SNTP & SNMP with Server and Client licenses, MQTT Controller must have at least one TCP/IP Ethernet port to for communication with master station over IEC-60870-5-104 without external protocol converter.
Type test certificate of the controller for IEC 60870-5-104 from NABL Accredited Laboratory /Any reputed international laboratory
10 | Time synchronization between FRTU, I/O modules, IEDs | Required on SNTP and direct pulse (1 PPS, 1 PPM). DCU shall have capability for Time Synchronization from Minimum 2 Server with priority selection
| Real time stamping at Controller level, I/O level | Required, Mandatory
11 | Response Time
| Digital Input | 1 msec or better
| Analog Measurement | 1 sec or better
| Digital Output | <1 sec or better
12 | I/O handling Capacity | Min 500 Physical Tags /Controller
13 | Pseudo Points (Digital, Analog) | Required
14 | Calculated Points (Digital, Analog) | Required
15 | SOE List storage | Min 500 (shall be user configurable)
| SOE list Retention Period | 1 Month
| Measurement Events | 500
16 | Fault Disturbance Recorder | 100 events
| FDR Retention Period | 1 Month
17 | Development of Interlock logic | Required, Mandatory
18 | Support of mathematical function - Arithmetic, Logical, Trigonometric functions, Differential and Integration functions, Timer, Counter etc. | Required, Mandatory
19 | Logic and Calculation functionality | Required, Mandatory
20 | Status LEDs on all module – for fault indication and Inputs / Outputs | Required
21 | Number of Multi Master Reporting possible with same ASDU | 5 Nos. (Mandatory)
22 | Web Based Monitoring | Required
23 | Software - All diagnostic tools, simulator tool, maintenance tools, configuration application for database and process control program development, documentation and maintenance | Required
24 | Engineering Functions | a) Configuration shall be possible both locally and remotely (Remote configuration over MODEM with static SIM )
b) Controller shall have multilevel passwords
c) On-line monitoring facility of real time data for monitoring/analysing the real time status of the process, program logic from the engineering station
f) Controller must have the provision to configure the IP of the redundant SCADA Systems (Socket IP)
25 | Battery Backup / Flash-PROM backup | Required if memory is volatile
26 | Auxiliary Power Supply | Redundant 18-72 VDC (24V DC) Supply with MCBs with add-on NO contact. The Controller shall have adequate protection against reversed polarity, over current and under voltage conditions, to prevent the internal logic from being damaged and becoming unstable causing mal-operation
27 | Auto-Startup and Restoration | In case of Power Supply Failure, Auto-Startup and Restoration of the Controller required
28 | Controller health monitoring contacts (CPU, Communication, I/O modules, Power Supply) | Required both Physical and Soft, Mandatory
29 | Environment Requirement, Reliability & Cooling | The Controller shall be capable of operating in ambient temperature from 0 to +65 degree C with rate of temperature change of 20 degree C/hour and relative humidity of 95%, non-condensing. Conformal coating is mandatory.
30 | DR Data Collection (Optional) | Support FTP protocol to transfer disturbance recorder data to remove server
31 | CPRI report for the product offered as per the GoI order no. 25-17/6/2018-PG dated 2nd July 2020 and subsequent order No. 12/34/2020-T&R dated 8th June 2021 | Cyber security compliance as per the enclosed letter of MoP. Type test certificate on cybersecurity compliance from NABL Accredited Laboratory / Any reputed international laboratory. Applicable standards are IEC 62351 series (specifically IEC 62351-100 parts 1 & 3), IEC 27036, IEC 20243 & IEC 62443)
32 | Battery Charger & Battery bank with proper rating of MCBs | 5 Amp FCBC Battery Charger / 6AH 2X12V Battery Bank
4.4 SINGLE PHASE POTENTIAL TRANSFORMER SUPPLY KIT (PT)
Sr. No. | Technical requirement | TPWODL Requirement | BIDDER RESPONSE
1 | Manufacturer’s name and country of manufacture | To be provided by bidder
2 | Type | Outdoor VT
3 | Installation type | Outdoor Resin Cast VT
4 | Rated Voltage / Highest System Voltage | 11kV/12kV or 33kV/36kV
5 | Insulation Class | E
6 | Rated frequency | 50Hz
7 | Conforming to Standard | IS16227-1&3
8 | No. of secondary windings | Single
9 | Rated System Voltage | 11kV
10 | Winding details | Enamel Copper Wire Winding
11 | Rated Primary Voltage | 11kV or 33kV
12 | Rated Secondary Voltage | 230 V
13 | Accuracy Class | 1
14 | Rated Secondary Burden | 500 VA(Burden calculation to be provided considering both FPI & AB switch power requirement)
15 | Rated Voltage Factor | 1.2 continuous & 1.9 for 8 hours
16 | Primary terminal material and details | Brass link
17 | Secondary terminal material and details | Brass Secondary terminal
18 | One minute power frequency withstand voltage test on primary winding | As Per IS 162227 – 1& 3
19 | Lightning impulse withstand voltage | As Per IS 162227 – 1& 3
20 | One minute power frequency withstand voltage test on secondary winding | As Per IS 162227 – 1& 3
21 | Total creepage distance (min) | 31 mm/kV
22 | Total weight of equipment
23 | Mounting details | As Per Drawing
24 | Measurement of Partial Discharge @ 1.2Um / √3 | As Per IS 16227 – 1& 3
25 | Measurement of Partial Discharge @ 1.2*Um | As Per IS 16227 – 1& 3
26 | Fuse protection on Secondary | YES
4.5 Lightning Arrestor
Sr. No. | Technical requirement | TPWODL Requirement | BIDDER RESPONSE
1 | Type | Polymeric type
2 | Rating | 9 kV or 30 kV rated 10 KA As per line requirement
3 | Class | Class DH as per IEC 60099-4
4 | Minimum continuous operating voltage | 7.65 kV MCOV & 20.78 kV MCOV
5 | Preferred Make | Raychem, Oblem, Elpro
6 | With an insulation class on HT terminal

## MODEM
4.2 DUAL SIM 5G/4G MODEM CUM ROUTER
Sr. No. | Technical requirement | TPWODL Requirement | BIDDER RESPONSE
1 | Product Description
1.1 | Make & Model | Bidder to provide Make & Model of proposed Cellular Modem. Also provide life cycle details
2 | Radio Interface
2.1 | Radio Interface | 5G Fall back to 4G/3G/2G
2.2 | Data interface | Cat 5 , Download and Upload 1000 Mbps
2.1 | Supported frequency band | 1. Modem should support multiband connectivity with FDD 5G & TDD 5G. 2. It should support Band 1, 3, 5, 8, 40 and Band 48. 3. The offered cellular modem should support and compatible to the data & radio interface of the network of public mobile service provider in Odisha City.
2.4 | Radio Transmitter Power | Vendor to provide details of radio transmitter power
2.5 | Receiver Sensitivity | Vendor to provide details of receiver channel sensitivity
2.6 | Cellular Module / Chip | Vendor shall give details of cellular chip /Module used along with datasheet
3 | Operating Condition
3.1 | Operating Temperature | -20 C to 70 C
3.2 | Operating Humidity | 5 % to 100 % (non -condensing)
3.1 | Power Consumption | Vendor to provide power consumption for idle and max during data transmission
3.4 | Storage /transport temperature | -40 °C to 85 °C
3.5 | MTBF | Vendor to provide details of MTBF
3.6 | Protection from pollution | Vendor shall provide design details such as protective paint /conformal coating on MCB, high grade electronic components uses to protect from environmental pollution.
4 | System Characteristics
4.1 | CPU | 1. Vendor to provide make & technical details of CPU used. 2. Vendor should also attached technical data sheet of CPU. 3. CPU usage should not crossed 40 % in typical operating & maintenance condition
4.2 | RAM | 1. Vendor to provide details of memory type, Speed & Size. 2. Usage of memory should not crossed 60 % in typical operating & maintenance condition
4.3 | Flash Storage | Vendor to provide details of flash storage Memory Provision to store system logs, event logs ,configuration file
5 | Mechanical Construction
5.1 | Dimension ( W X H X D) | Vendor to provide details of Dimension ( W X H X D)
5.2 | Weight in Kg | Vendor to provide details of Weight in KG
5.3 | Housing | Metal Preferred Aluminum alloy having better heat dissipation & ruggedness
5.4 | Mounting | DIN rail Mounting
5.5 | Degree of Protection | IP30
6 | Interface/Port Type
6.1 | Ethernet | 1. Minimum 2 X RJ45 Port Ethernet, Speed 10/100 Mbps auto negotiable having status LED indication. 2. Port should be configurable as LAN /WAN as required.
6.2 | Cellular interface | 1. Cellular modem should have dual SIM provision. 2. Dual SIM for network redundancy /backup. 3. Dual SIM operation ensures that the cellular connection is always available. 4. It will automatically disconnect the 1st SIM card’s low/weak cellular connection and will reconnect to establish a stronger connection using the 2nd SIM card.
6.3 | Ethernet Cable (CAT 4) | Vendor to provide Ethernet Cable (CAT 6) minimum 1.5 M
7 | Software Features / Supported protocols
7.1 | Network Protocols | TCP/IP ,UDP/IP, HTTP, ARP,DHCP, ICMP, SNMP, V1/V2 &V1, NTP, SSL/TLS
7.2 | Routing | Astatic Routing, RIP 1 &2 ,OSPF V2 &V1
7.3 | VPN | Open VPN , IP Sec, L2TP, PPTP, GRE
7.4 | Alarm Message | Device shall have alarm notification on SNMP trap
7.5 | Management /Monitoring | 1. Cellular modem should shall support Local /Remote management through web HTMLS, SSHP & Telnet 4. 2. It shall support monitoring through system logs & SNMP version V1/V2 & V3. 3. Notification & command shall be possible over SMS. 4. Firmware upgradation through Web, backup & restore of configuration shall be possible.
7.6 | Operating System | Vendor to give the details of operating system & its Version
7.7 | Application | Vendor to give the details of application & package installed in modem
7.8 | AT Command Support | YES /NO
7.9 | Scheduled rebooting | Device should be capable to program auto rebooting as per configured / scheduled configured scheduled time.
7.1 | Watch dog feature | Modem Shall have feature of tracking data connectivity status by periodic ping test and switchover on backup.
7.11 | Factory Reset | Provision of Resetting the device for factory configuration.
7.12 | Diagnosis Feature | Device Shall support real time diagnostic such as active connection ,traffic on interfaces
7.13 | SCADA Protocols | 1. Transparent Mode: The modem should be capable for communicating with multiple protocol RTUs in Transparent Mode 2. DLMS Master Mode: The modem should be capable to reading multiple DLMS meters connected to it. 3. Modbus Master Mode: The modem should be capable of reading Multiple Modbus Meters connected to it. 4. Data Segregation Mode: modem should segregate the collected data as per Instantaneous Parameters, Billing, Load Profile and Tamper parameters in separate files per Meter. 5. IEC 104 – 104 Master – Multi Slave Mode: The modem should be capable to reading RTUs in IEC60870-5-104 protocol and communicate with SCADA system on IEC 60870-5-104 protocol upto 8 masters. Adequate data interlock mechanisms should be implemented to avoid data loss. 6. IEC 104 Slave mode Multi Master support 7. DNP3 Slave mode with Integrity poll, Static, Event data, Class 0,1,2,3 support 8. Other Data Sending Modes: modem should support TCP, UDP, HTTPS, MQTT data sending formats 9. Simultaneous Operations of multiple protocols. Ex modem should be capable of sending Modbus Data over 104 and MQTT simultaneously
8 | Security
8.1 | Security | HTTPs, SSH, Authentication with RADIUs or TACACS + , activate cellular interface with SMS ,Ethernet 802 .1X(EAPPEAP/MsCHPv2 or EAP -TLS
8.2 | Authentication | User Management (local ,RADIUS, TACACS+ , Mixed )
8.3 | State inspection firewall | Static firewall IPv4 / IPv4 with incoming and forwarding ruleset ,DoS protection ,IP/Port/Protocol filtering ,NAT
9 | Antenna
9.1 | No Of Antenna | The 5G Cellular modem Should have two antenna connection (MIMO).One is primary cellular antenna & second is diversity antenna(MIMO)
9.2 | Cable Length | Cable should have Low loss RF Cable with minimum 5M
9.3 | Type of Antenna | Antenna Should be Omni directional with high gain (High gain ≥5)
9.4 | Construction of antenna | It should be Steady ,good quality material ,water/ weather proof having adequate gold plate connector compatible with cellular modem antenna. Port. It should be suitable mounting arrangement to installed indoor
9.5 | Frequency Band, impedance & Polarization | Vendor Shall provide the details of frequency Band. Antenna should be compatible with offered device & network service provide with frequency band, port impedance & radio signal polarization
9.6 | VSWR | Vendor Shall provide details of VSWR
9.7 | Gain of antenna | Vendor Shall provide Gain details of primary & secondary antenna
10 | Power Supply
10.1 | Power Supply | 24V(As per controller DC supply)
10.2 | Connector Type | Modem Should have preferable screw type firm connection. It should have reverse polarity protection & surge protection
11 | Status & diagnostics indicator
11.1 | LED indicator | Vendor to provide details of status & diagnostics indicator. (Power- ON & OFF ,ERR- Error Red, Signal, network, SIM status)
12 | Certification:- IEC Specified as below or equivalent to international Standard
12.1 | Electrostatic discharge immunity test | IEC EN 61000-4-2
12.2 | Radiated, radio-frequency, electromagnetic field immunity test | IEC EN 61000-4-1
12.3 | Electrical fast transient/burst immunity test | IEC EN 61000-4-4
12.4 | Surge immunity test | IEC EN 61000-4-5
12.5 | Immunity to conducted disturbances, induced by radio-frequency fields | IEC EN 61000-4-4
12.6 | Information technology equipment –Safety | IEC 60950
12.7 | Environmental testing-Vibration (sinusoidal) | IEC 60048-2-4
12.8 | Environmental testing-Shock | IEC 60048-2-27
12.9 | Environmental testing-Free Fall (withdrawn) | IEC 60048-2-12
12.1 | Proof of check | vendor should give one number of modem along with Technical offer for performance & application compatibility check for period of minimum 15 days
12.11 | Country of manufacturing | Vendor to provide Country of manufacturing details
12.12 | Service Centre in India | Vendor to provide details of Service Centre in India
12.13 | Regulatory compliance | Vendor shall confirm that offered product is compiled & certified by all Indian government bodies related to telecommunication/ wireless communication (WPC ,DOT) to operate &user this product in country . Vendor to share compliance certificate of the same
12.14 | Surge protection /electrical isolation | It should be available on all Ethernet communication port & power supply input vendor shall share certification
12.15 | Environmental Condition | Cyclonic environment with wind velocity up to 250kmph. Some of the regions, where the work will take place includes coastal areas, subject to high relative humidity, which can give rise to condensation. Onshore winds will frequently be salt laden. On occasions, the combination of salt and condensation may create pollution conditions for electronic equipment. Some places are in heavily industrial polluted areas. Therefore, all supplied material and equipment shall be designed and protected for use in exposed, heavily polluted, salty, corrosive and humid coastal atmosphere.

## Battery & battery charger
4.3 BATTERY & BATTERY CHARGER
Sr. No. | Technical requirement | TPWODL Requirement | BIDDER RESPONSE
A.1 | Make of Battery Charger | To be provided by bidder
A.2 | Model of Battery Charger | To be provided by bidder
B.1 | Make of Battery | To be provided by bidder
B.2 | Model of Battery | To be provided by bidder
1 | Scope | The battery & battery charger are intended for operating FPI DCUs. The battery should capable of providing back up for minimum 8 hours for operationalisation of DCU/4G Modem.
2 | Average Number of Operations | Not Applicable
3 | Standards | IS 1885/IEC 600504, IS -15549/2005
4 | Climate | Must able to operate efficiently considering hot & humid climate of Odisha region. The battery shall be capable of operating satisfactorily in outdoor applications when it is housed in a Cubicle between 10 deg. C and 65 deg.C and in locations where the relative humidity between 30% to 100%
5 | Battery Ratings
5.1 | Voltage | 24 VDC specified at 27 deg.C.
5.2 | Battery Type | SMF,VRLA with chargers of conventional type
5.3 | Voltage/cell | 12 volts
5.4 | Capacity of Batteries | 7 AH,5 Amps(Battery rating to be calculated considering FPI and motorized AB switch power requirement for)
5.5 | Connecting cables | Cable size selection should provide the lowest voltage Drop possible between battery system and operating Equipment.
5.6 | Method of charging | Constant voltage method and current limit(variable Current)
5.7 | Efficiency | Not less than 90% at full rated load
6 | Battery Charger Rating
6.1 | Battery Charger type | Constant Voltage and Current limiting charger. Charger with inbuilt battery health monitoring is highly preferable.
6.2 | Charger Input Voltage | Single phase (2 wire) voltage 250V AC +30% to -20% Frequency 50Hz ± 5%.
6.3 | Charger Output
6.3.1 | Regulation | ± 1%
6.3.2 | Charger current | 5 Ampere
6.3.3 | Efficiency | Not less than 85% at full rated load
6.3.4 | Current limit | 110% of rated load
6.3.5 | Insulation | Not less than 5 mega Ohms.
i. between DC output terminals and AC input terminals.
ii. Between AC input terminals and earth
6.3.6 | Indication | The charger shall have suitable indicators to visually know its mode of operation. Charger indication as below must be available:
Mains on (Red LED), Charger on (Yellow), Boost on (Yellow LED), Float on (Green LED) and Battery reverse polarity (Red LED), O/p DC fuse blown (Red LED) LED lamp indication. (LED colors can be changed)
6.3.7 | Protection | Input single pole MCB’s for AC & DC of 10 Amperes separate for battery & charger.
The battery charger must include protections like:
i) AC input MCCB & ELBS with input ON/OFF switch and fuses/ contactor.
ii) DC output MCCB with output ON/OFF switch and fuses.
iii) Current limit protection, soft start feature, surge suppressor.
iv) Fast semiconductor fuses for rectifier bridge.
v) Charger over load / short circuit vi) Battery polarity reverse, Battery Over/Under voltage, Charger rectifier fail, etc.
6.3.9 | Battery & charger Alarms | Potential free contacts must be available to integrate with SCADA for abnormality if any. Most preferred alarms are like: AC supply fail, DC supply fail, Battery Low, Battery Fail, Battery Charger fail, Battery polarity reverse. Serial Communication is preferred.
6.3.8 | Cooling | External exhaust fan(Optional)
6.4 | Climate | Must able to operate efficiently considering hot & humid climate of Odisha region. The battery shall be capable of operating satisfactorily in outdoor applications when it is housed in a Cubicle between 10 deg. C and 65 deg.C and in locations where the relative humidity between 30% to 100%
6.5 | Wiring | The internal wiring of the charger shall be carried out with PVC insulated
6.6 | Accessibility | 650V grade standard copper conductor. The control wiring shall be carried out with 2.5 Sq.mm copper conductors.
All the important components of the charger must be easily accessible for maintenance, repair, and replacement in case of trouble without giving interruption to total D.C. supply as far as possible.