## ANNEXURE-1
OUTDOOR VCB
ANNEXURE- 1
SL. NO. | Description | Remarks
1 | Panel illumination and space heating | AC MCB rating shall be 16 A
Space heater capacity shall be at least 80W
Hygrostat shall be provided
2 | Material of Hardware (Bolts, Nuts, Washers, Spring Washers etc.) | SS for M10 and below, HDG for above sizes
3 | Tripping Circuit and Closing coil circuit | Breaker shall be supplied with Two Tripping Circuit and Closing coil circuit with independent and separate DC MCBs (3 nos)
Conventional tripping coil needs to be provided instead of an Electronic coil
4 | Terminal Connector | Concern TP Odisha DISCOM to confirm during release of RO (i.e. DOG/COYOTE/Panther/Zebra)
5 | Control Voltage | Concern TP Odisha DISCOM to confirm during release of RO (24VDC/48VDC)
6 | Locking provision | Castle key is required for safe local Maintenance of VCB
7 | Spring charging Motor | Shall be universal type with suitable ratings of MCB
8 | Rating of Trip Coil and Close Coil | Burden and Resistance to be mentioned during GTP /Drawing approval
9 | Door Access | Provision of additional stand at back side for VCB Back Door Access
10 | Angle Size | 75x75x6 mm for structure and additional support structure to be considered in between CT Mounting Structure and VCB
11 | Local remote Selection switch | To be provided by OEM
12 | Closing and Opening Time of Breaker | Closing and Opening Time shall not be changed w.r.t Voltage variation within 85% to 110% and 70% to 110% respectively
13 | Nut and Bolts | 3 Nos of Nuts are required instead of 2 for each Mounting structure

## GTP
OUTDOOR VCB
S. No. | Particulars | Requirements |  |  | OEM/Bidder's Response
|  | 11kV | 33 kV | 66Kv
4.1 | Application | Outdoor | Outdoor | Outdoor
4.2 | Type | VCB | VCB | SF06
4.3 | Rated voltage | 12KV | 36 kV | 72.5kV
4.4 | Service voltage | 11KV | 33 kV | 66kV
4.5 | Rated Frequency | 50 Hz | 50 Hz | 50 Hz
4.6 | Number of phases | 3 | 3 | 3
4.7 | Rated insulation level
4.7.1 | Rated Lightning impulse withstand voltage
a | To earth and b/w Poles | 75 kVp | 170 kVp | 325kVp
b | Across the isolating distance | 75 kVp | 195 kVp | 325kVp
4.7.2 | Rated short duration power frequency withstand voltage
a | To Earth and between Poles (Dry test for 1 Min) | 28 kV | 70 kV | 140kV
b | To Earth and between Poles and across the isolating distance (Wet test for 10 Sec) | 28 kV | 75 kV | 140kV
c | Across Open Switching Device |  | 75 kV
4.8 | Rated normal current | 1250 A | 1250 A /2000 A | 1600 A
4.9 | Rated load breaking current (sym) | 25 kA | 25 kA(rms) | 31.5 kA (rms)
4.1 | Percentage DC component | <40 % | <50 % | <50 %
4.11 | Rated short circuit withstand current for 3 seconds | 25 kA | 25 kA(rms) | 31.5 kA (rms)
4.12 | Rated short circuit making current | 62.5 kA | 62.5kA | 78.75 kA
4.13 | First Pole to Clear factor | 1.5 for Terminal fault
1 for Short line fault
2.5 for Out of phase fault
4.14 | Rated capacitive switching currents
4.14.1 | Rated line charging breaking current | As per IEC 62271-100 | 10 A (rms) | 10 A (rms)
4.14.2 | Rated cable charging breaking current | 25 A (rms) | 50 A (rms) | 125 A (rms)
4.14.3 | Rated single capacitor bank breaking current | 400 A (rms) | 400 A (rms) | 400 A(rms)
4.14.4 | Capacitor Banks with series reactors switching capacity | Suitable for 7.62MVAr capacitor banks with Series Reactors | Suitable for 14.4MVAR Capacitor Banks with series reactors | Suitable for 28.8 MVAR Capacitor Banks with series reactors
4.15 | Maximum switching over voltages for cable charging & capacitor bank breaking current
4.16 | Rated operating sequence | 0-0.3sec-CO-3min-CO
4.17 | Total Break time(max) | 45 ms (Shall not change during operating life) | 45 ms(Shall not change during operating life) | 45 ms(Shall not change during operating life)
4.18 | Closing time (max) | 60 ms (Shall not change during operating life) | 60 ms(Shall not change during operating life) | 60 ms(Shall not change during operating life)
| CO Time (max) | 100ms
| Spring charging time | <15 s
4.19 | Rated supply voltage of control circuits | 220/110/48/24V DC *Control Voltage will be shared by concern TP DISCOM at the time of release of RO/PO
4.19.1 | Range for satisfactory operation of Trip circuit | 70% to 110%
4.19.2 | Range for satisfactory operation of closing & other circuits | 85% to 110%
4.2 | Transient recovery voltages | As per IEC 62271-100
4.21 | No. of auxiliary contacts | 10 NO & 10 NC
4.22 | Clearance in air (As per IEC 62271-100)
4.22.1 | Between phases | 300 mm | 320 mm | 630 mm
4.22.2 | phase to earth | 370 mm | 320 mm | 630 mm
4.23 | Min. creepage distance of insulator | 31mm per kV
4.24 | Degree of Protection | IP 55
4.25 | Operating mechanism | Spring charged by universal motor.
4.26 | Operation | Gang operated
4.27 | Temp. rise at rated normal current | As per IEC 62271-100
4.28 | Minimum Vertical clearance of live conductor from ground level | As per CEA guidelines
4.29 | Mechanical Endurance | M2
4.3 | Electrical Endurance | E2 with Auto reclosing | E2 with Auto- reclosing | E1 / E2
4.31 | Restriking Class | C2
4.32 | Class | S2
4.33 | Material of main contact | Should be as that in Clause 5.6.1
4.34 | Interrupter | Vacuum Interrupter should be of same make as that of Breaker manufacturer. Representative shall visit Interrupter manufacturing Facility during Factory Inspection.
4.36 | Contact Resistance | <30 µΩ (shall not change by ±10% during operating life)
4.37 | Panel illumination and space heating | Shall be suitable for 240V AC±10% Space Heater – min. 80 W Thermostat – 300C to 1100C LED Lamp with holder – 5 W Door Limit Switch – 6A 3Pin Switch & Socket – 15 A Control Fuse with Base – 6A DP AC MCB – 6A, 10kA I/C AC & DC MCB rating should be 16 A
4.38 | Anti-pumping features | Yes (Anti pumping ckt should be connected with 52a & its own contact in parallel.)
4.39 | Total Weight | Bidder to provide
4.4 | Dimensions | Bidder to provide
4.42 | No. of operations
4.42.1 | At rated normal current | Bidder to provide
4.42.2 | At rated capacitor bank breaking current | Bidder to provide
4.42.3 | At SC breaking current | Bidder to provide
4.43 | No. of Breaks per phase | 1 | 1 | 1
4.44 | SF6 Low & Lockout Alarm | - | - | To be provided
4.45 | Min. Operating Pressure @200C | NA | NA | Bidder to provide
4.46 | Low SF6 Gas Pressure @200C | NA | NA | Bidder to provide
4.47 | Nominal Operating Pressure @200C | NA | NA | Bidder to provide
4.48 | Permissible Gas leakage | NA | NA | Max. 1% per year
4.49 | Qty. of Gas | Bidder to provide
FOR VCB Type
a. | Type of indication for contact erosion
b. | Rating of interrupter
c. | Make of interrupter
d. | Connectors
e. | Type test certificates
f. | Test for Re-strike free for VCB
g. | Total weight of breaker (Kg)
h. | Dimensions (mm)