## Sheet1
Sl. No. | Parameters | TPCODL/TPNODL/TPSODL/TPWODL Requirements
|  | 48 V/200AH | 24V/150AH | OEM/Bidder's Response
A | Battery Charger
1 | AC input voltage | 415 V + 20% AC, 3 | 415 V + 20% AC, 3
|  | Phase, 4 Wire | Phase, 4 Wire
2 | AC input frequency | 50 Hz + 5 % | 50 Hz + 5 %
3 | DC Output Current rating | 50 A | 40A or 70 A
4 | DC output voltage settings: | Nominal: 48V; Range: 48 V DC to 54 V DC for FC Range: 48 V DC to 62V DC for FCBC | Nominal: 24V; Range: 24 V DC to 27 V DC for FC Range: 24 V DC to 31V DC for FCB
5 | Output Voltage Regulation | ± 1 % of set output voltage value for +15% to -15% input voltage variations and for 10-100% of load variations | ± 1 % of set output voltage value for +15% to -15% input voltage variations and for 10-100% of load variations
6 | Efficiency | > 80% | > 80%
7 | Power Factor | > 0.85 | > 0.85
8 | Ripple voltage | < 200mV (P-P) | < 200mV (P-P)
9 | Galvanic Isolation | The rectifier stage must have galvanic isolation | The rectifier stage must have galvanic isolation
10 | Switchgear:
| a) input side (AC) | 4 pole, 25A/20 kA or suitable size MCCB | 4 pole, 25A/20 kA or suitable size MCCB
| b) output side (DC) | 2 pole, 100A MCCB suitable for DC operation | 2 pole, 100A MCCB suitable for DC operation
11 | Protections | a) Surge suppressors at Both Source and Load side | a) Surge suppressors at both source and load side
|  | b) Soft start | b) Soft start
|  | c) Battery charger current limit | c) Battery charger current limit
|  | d) Control circuit & Voltmeter fuses | d) Control circuit & Voltmeter fuses
|  | e) Rectifier protection | e) Rectifier protection
|  | f) Blocking diode | f) Blocking diode
|  | g) Under voltage & over voltage | g) Under voltage & over voltage
|  | h) Short circuit and Overload | h) Short circuit and Overload
|  | i) Thermal protection (Fire safety protection) | i) Thermal protection (Fire safety protection)
|  | k) Wrong battery connection/reverse polarity | k) Wrong battery connection/reverse polarity
|  | l) Battery Earth Fault | l) Battery Earth Fault
|  | m) POWER ON self-test | m) POWER ON self-test
|  | n) Supply wrong phase, phase failure | n) Supply wrong phase, phase failure
12 | Operating temperature | 0⁰C to 55⁰C | 0⁰C to 55⁰C
13 | Bus bars (copper) | Suitable size for carrying 100 A (min.) current. | Suitable size for carrying 100 A (min.) current.
14 | Connection to back- up battery bank, load and battery at site | through dedicated MCBs via bus-bar- | through dedicated MCBs via bus-bar-
15 | Mounting arrangement | Cabinet/ rack | Cabinet/ rack
16 | Ingress Protection | IP 42 | IP 42
17 | Cooling arrangement | suitable cooling arrangement (natural/ forced air with fan) should be provided | suitable cooling arrangement (natural/ forced air with fan) should be provided
18 | Alarms (at LCD display of Battery Charger (FC & FCBC) | AC Mains Fail/MCB trip (at charger input) | AC Mains Fail/MCB trip (at charger input)
|  | DC Fail/MCB trip (at charger output to load) | DC Fail/MCB trip (at charger output to load)
|  | DC Fail/MCB trip (at charger output to battery) | DC Fail/MCB trip (at charger output to battery)
|  | AC under-voltage - | AC under-voltage -
|  | AC over-voltage | AC over-voltage
|  | DC load under- voltage | DC load under- voltage
|  | DC load over- voltage | DC load over- voltage
|  | Charger Under Voltage | Charger Under Voltage
|  | Charger Over Voltage | Charger Over Voltage
|  | Fault at rectifier module- | Fault at rectifier module-
|  | Battery Earth Fault | Battery Earth Fault
19 | Microprocessor based Digital Controller form to suit SCADA Compatibility through MODBUS (Serial) Protocol and Controller shall have display feature
20 | AI Signals for SCADA Communication | Float Voltage Boost Voltage Float Current Boost Current Load Voltage Load Current Battery Voltage Battery Current DC Leakage Incomer Voltage and Current
21 | Additionally, Analog meter dedicated for monitoring of DC leakage to be provided.
22 | The controller should be configurable with desired baud rate, slave ID no. Parity bits from display or push button at site.
23 | LED indications | Charger ON (Green)- | Charger ON (Green)-
|  | Charger fail -Alarm (Red) | Charger fail -Alarm (Red)
|  | Charger over temperature (Red) | Charger over temperature (Red)
|  | Charger under voltage (Red) | Charger under voltage (Red)
|  | SCR Fuse Fail (Red) | SCR Fuse Fail (Red)
|  | AC mains ON (Green) | AC mains ON (Green)
|  | AC mains Fail (Green) | AC mains Fail (Green)
|  | Float ON (Green) | Float ON (Green)
|  | Boost ON (in FCBC Only)- Amber | Boost ON (in FCBC Only)- Amber
|  | Phase Failure/wrong phase | Phase Failure/wrong phase
|  | Charge/Discharge | Charge/Discharge
|  | Charger Overload | Charger Overload
|  | Output Fail | Output Fail
|  | Battery Low | Battery Low
B. | Housing Cabinet
1 | Dimensions (L X B X H) | To be provided by bidder | To be provided by bidder
2 | Suitable for containing the charger | Yes/ No | Yes/ No-
3 | Structure | Steel rack/cabinet, painted with anti- corrosive paint. | Steel rack/cabinet, painted with anti- corrosive paint.
4 | Ingress protection | IP 42 | IP 42
C. | DCDB
| Item Description | Functionality Expected
1 | Feature of DCDB feeder ON/OFF status monitoring through controller display | Required
2 | Feature of DCDB earth fault monitoring through controller display | Required
3 | I/C feeder comprising of copper busbar double pole DC MCCB - 300 A | 2 Nos.
4 | O/G feeder comprising of double pole 25A MCB | 15 Nos
5 | Moving coil DC voltmeter of size 96 sq. mm with HRC fuse 0-300 V | 1 No.
6 | Moving coil DC ammeter of size 96 sq. mm; 0-150 Amp | 1No.
7 | Copper bus bar (size to be mentioned by bidder) | Copper Bus Bar
8 | Dropper Diode scheme | Required
9 | Surge Protection device (SPD) class at both source and load side | Type#1
10 | Earthing bus bar, double earthing provision | 25 x 3 sq. mm tinned copper
11 | Cooling | Speed Regulated Fan Cooled
12 | Digital Leakage Current Indicator | Yes
13 | Lamp indication to be provided whether battery charger is running on Float mode or Boost Mode | Yes