## 33kV .
METERING CUBICLE:
Sr. No. | Particulars | Parameters
1 | Normal system voltage (kV r.m.s) | 33
2 | Highest system voltage (kV r.m.s) | 36
3 | Frequency | 50HZ
4 | Number of Phases | 3
5 | Impulse withstand voltage (KVpeak) (on assembled CT-PT set) | 170 KVpeak
6 | Power frequency dry withstand test on
| (a) primary winding | 70kV (rms)
| (b) secondary winding | 3kV (rms)
7 | Maximum temperature rise over maximum ambient temperature of 450C at rated continuous thermal current at rated frequency and with rated burden. | 1100C (As per IS 16227-1 for Class F Insulation)
8 | Cable connection terminal of CT to base plate distance | 950mm Minimum
9 | Paint (Powder Coating) | RAL 7032
10 | Powder Coating Thickness | 80 microns
11 | Rating/Size of Bus Bar | Tinned Electrolytic Copper Bus Bar size suitable for all rating of metering cubicle shall be 600A
11.a | Maximum Current Density of Copper Bus Bar | 1.75 A/sqmm
12 | Enclosure
a. | Material and thickness of the meter box | 3mm GI Sheet with Powder Coating, min. thickness of powder coating shall be 80micron. The paint should sustain for harsh environment & saline weather, Corrosion Protection for Panel entire life cycle (minimum 10 yrs).
b. | Non-current carrying nuts, bolts, screws etc. on enclosure | SS 304
c. | Protection against penetration of dust and water | IP 55
d. | Door of metering compartment | Wire Mess & Door of metering compartment
e. | Size of Enclosure (max. allowed) | 2400mm (Height) X 1400mm (Length) X 1600mm (Depth) and suitable to inhouse upto CTR 600/5A
f. | Outdoor Application, if required | Suitable Canopy will be provided in outdoor application, so that meters can be viewed properly
g. | System Earthing | Suitable for 25kA/1sec
h. | Size of Earth Bus Bar | 25x3mm Copper
(This copper bus to be connected to both side M16 Earth Bolt)
i. | Washers and connectors | Bi-metallic washer and tinned copper connector
j. | Cable cleat | HDPE/Nylon Fire retardant cable cleat
k. | Incoming & Outgoing Cable Cleating Arrangement | Suitable for 3Cx400 sqmm and 1Cx630 sqmm
(Actual size of cable to be provided during drawing approval stage)
CURRENT TRANSFORMERS:
Sr. No. | Particulars | Parameters
1 | Normal system voltage (kV r.m.s) | 33
2 | Highest system voltage (kV r.m.s) | 36
3 | Frequency | 50HZ
4 | Type | Single Phase Indoor Resin Cast
5 | Number of CT | 3Nos
6 | Rated output (VA burden) | 10VA.
7 | Rated continuous thermal current | 1.2 times of rated primary current
8 | Short time current rating for 1 sec. | · 30/5A CT Ratio to 75/5A CT Ratio – 13.1kA/1sec
· 100/5 CT Ratio upto 600/5A - 25kA/1sec
9 | Rated dynamic current (Peak) | 2.5 times of short time thermal current rating
10 | Instrument security factor | ≤ 5
11 | Impulse withstand voltage (KVpeak) (on assembled CT-PT set) | 170 KVpeak
12 | Maximum temperature rise over maximum ambient temperature of 450C at rated continuous thermal current at rated frequency and with rated burden. | 1100C (As per IS 16227-1 for Class F Insulation)
13 | Type of Insulation
13.1 | Impregnation | Class H vacuum pressure impregnation
13.b | Varnish on CT-PT windings | Class H varnish
13.c | Epoxy resin casting | Class F Resin
14 | Limits of current (ratio) Error and phase Displacement. (For 0.2S Accuracy class) | Within limited of IS:16227 with latest amendment/revision
15 | Max. ratio error | Within limited of IS:16227 with latest amendment/revision
16 | Max. phase angle error | Within limited of IS:16227 with latest amendment/revision
17 | System condition | Effectively earthed system
18 | Thickness of base plate | 5mm, Plate shall be properly with earthing arrangement
19 | Type | Dry type epoxy resin cast
20 | Creepage distance | 900mm
(It is only applicable for Insulator connecting for CT, PT & Cable
Compartment, if used)
21 | Transformation ratio/ CT ratio | As per above schedule of requirement.
22 | No. of cores | 1 Nos
23 | Rated continuous thermal current temperature rise over ambient | As per IS 16227 latest amendment/revision
24 | One minute power frequency voltage withstand test on secondary winding | 3kV
25 | Class of accuracy | 0.2S
26 | Secondary termination | S1 & S2 shall be clearly marked
27 | CT primary current | Shall be as per tender
(30A, 50A, 75A, 100A, 150A, 200A, 300A, 400A, 600A)
28 | CT secondary current | 5A
29 | Total weight of the core before casting of | To be provided by Bidder
Resin
30 | Total weight of the unit after casting of Resin | To be provided by Bidder
31 | Power frequency dry withstand test on
| (a) primary winding | 70kV (rms)
| (b) secondary winding | 3kV (rms)
32 | Washers and connectors | Bi-metallic washer and tinned copper connector
33 | CT terminal shape | L-shaped or cross flat type
34 | Rating/Size of Bus Bar | Tinned Electrolytic Copper Bus Bar size suitable for all rating of metering cubicle shall be 600A
POTENTIAL TRANSFORMERS:
Sr. No. | Particulars | Parameters
1 | Normal system voltage (kV r.m.s) | 33
2 | Highest system voltage (kV r.m.s) | 36
3 | Frequency | 50HZ
4 | Type | Single Phase Indoor Resin Cast
5 | Number of phases | Single phase
6 | No of PT | 3 Nos
7 | Rated Output (VA) Burden | 30VA
8 | Transformation ratio (PT ratio) | 33KV/√3/ 110V/√3
9 | Impulse withstand voltage | 170
(KV peak) (on assembled CT PT set)
10 | One minute power frequency dry withstand voltage (on assembled CT-PT set)
(a) Primary (KV rms)
| (b) Secondary (KV rms) | 70kV
3kV
11 | Class of accuracy | 0.2
12 | Rated voltage factor and time | 1.2 times continuous and 1.5 times for 30 sec
17 | System condition | Effectively earthed system
18 | Maximum temperature raise over maximum ambient temperature (which may be taken as 450C) at rated frequency and with rated Burden | Within limited of IS: 16227 with latest amendment/ revision.
19 | Maximum ratio error | Within limited of IS: 16227 with latest amendment/ revision.
20 | Maximum phase angle error | Within limited of IS: 16227 with latest amendment/ revision.
21 | Type of Insulation
21.a | Impregnation | Class H vacuum pressure impregnation
21.b | Varnish on CT-PT windings | Class H varnish
21.c | Epoxy resin casting | Class F Resin
22 | Creepage distance | 900mm
(It is only applicable for Insulator connecting for CT, PT & Cable
Compartment, if used)
21 | Basic insulation Level | 36/70/170 KV
22 | Thickness of baseplate | 5mm, Plate shall be properly with earthing arrangement.
23 | Material of Bushings | Epoxy
24 | Material for Rod of Bushings | Copper (if Applicable)

## 11KV
METERING CUBICLE:
Sr. No. | Particulars | Parameters
1 | Normal system voltage (kV r.m.s) | 11
2 | Highest system voltage (kV r.m.s) | 12
3 | Frequency | 50HZ
4 | Number of Phases | 3
5 | Impulse withstand voltage (KVpeak) (on assembled CT-PT set) | 75 KVpeak
6 | Power frequency dry withstand test on
| (a) primary winding | 28kV (rms)
| (b) secondary winding | 3kV (rms)
7 | Maximum temperature rise over maximum ambient temperature of 450C at rated continuous thermal current at rated frequency and with rated burden. | 1100C (As per IS 16227-1 for Class F Insulation)
8 | Cable connection terminal of CT to base plate distance | 750mm Minimum
9 | Paint (Powder Coating) | RAL 7032
10 | Powder Coating Thickness | 80 microns
11 | Rating/Size of Bus Bar | Tinned Electrolytic Copper Bus Bar size suitable for all rating of metering cubicle shall be 400A
11.a | Maximum Current Density of Copper Bus Bar | 1.75 A/sqmm
12 | Enclosure
a. | Material and thickness of the meter box | 3mm GI Sheet with Powder Coating, min. thickness of powder coating shall be 80micron. The paint should sustain for harsh environment & saline weather, Corrosion Protection for Panel entire life cycle (minimum 10 yrs).
b. | Non-current carrying nuts, bolts, screws etc. on enclosure | SS 304
c. | Protection against penetration of dust and water | IP 55
d. | Door of metering compartment | Wire Mess & Door of metering compartment
e. | Size of Enclosure (max. allowed) | 1700mm (Height) X 1000mm (Length) X 1200mm (Depth) and suitable to inhouse upto CTR 400/5A
f. | Outdoor Application, if required | Suitable Canopy will be provided in outdoor application, so that meters can be viewed properly
g. | System Earthing | Suitable for 25kA/1sec
h. | Size of Earth Bus Bar | 25x3mm Copper
(This copper bus to be connected to both side M16 Earth Bolt)
i. | Washers and connectors | Bi-metallic washer and tinned copper connector
j. | Cable cleat | HDPE/Nylon Fire retardant cable cleat
k. | Incoming & Outgoing Cable Cleating Arrangement | Suitable for 3Cx400 sqmm & 1Cx400 sqmm
(Actual size of cable to be provided during drawing approval stage)
CURRENT TRANSFORMERS:
Sr. No. | Particulars | Parameters
1 | Normal system voltage (kV r.m.s) | 11
2 | Highest system voltage (kV r.m.s) | 12
3 | Frequency | 50HZ
4 | Type | Single Phase Indoor Resin Cast
5 | Number of CT | 3Nos
6 | Rated output (VA burden) | 10VA.
7 | Rated continuous thermal current | 1.2 times of rated primary current
8 | Short time current rating for 1 sec. | · 30/5A CT Ratio to 75/5A CT Ratio – 13.1kA/1sec
· 100/5 CT Ratio upto 400/5A - 25kA/1sec
9 | Rated dynamic current (Peak) | 2.5 times of short time thermal current rating
10 | Instrument security factor | ≤ 5
11 | Impulse withstand voltage (KVpeak) (on assembled CT-PT set) | 75 KVpeak
12 | Maximum temperature rise over maximum ambient temperature of 450C at rated continuous thermal current at rated frequency and with rated burden. | 1100C (As per IS 16227-1 for Class F Insulation)
13 | Type of Insulation
13.a | Impregnation | Class H vacuum pressure impregnation
13.b | Varnish on CT-PT windings | Class H varnish
13.c | Epoxy resin casting | Class F Resin
14 | Limits of current (ratio) Error and phase Displacement. (For 0.2S Accuracy class) | Within limited of IS:16227 with latest amendment/revision
15 | Max. ratio error | Within limited of IS:16227 with latest amendment/revision
16 | Max. phase angle error | Within limited of IS:16227 with latest amendment/revision
17 | System condition | Effectively earthed system
18 | Thickness of base plate | 5mm, Plate shall be properly with earthing arrangement
19 | Type | Dry type epoxy resin cast
20 | Creepage distance | 300mm
(It is only applicable for Insulator connecting for CT, PT & Cable
Compartment, if used)
21 | Transformation ratio/ CT ratio | As per above schedule of requirement.
22 | No. of cores | 1 Nos
23 | Rated continuous thermal current temperature rise over ambient | As per IS 16227 latest amendment/revision
24 | One minute power frequency voltage withstand test on secondary winding | 3kV
25 | Class of accuracy | 0.2S
26 | Secondary termination | S1 & S2 shall be clearly marked
27 | CT primary current | Shall be as per tender
(30A, 50A, 75A, 100A, 150A, 200A, 300A, 400A)
28 | CT secondary current | 5A
29 | Total weight of the core before casting of | To be provided by Bidder
Resin
30 | Total weight of the unit after casting of Resin | To be provided by Bidder
31 | Power frequency dry withstand test on
| (a) primary winding | 28kV (rms)
| (b) secondary winding | 3kV (rms)
32 | Washers and connectors | Bi-metallic washer and tinned copper connector
33 | CT terminal shape | L-shaped or cross flat type
34 | Rating/Size of Bus Bar | Tinned Electrolytic Copper Bus Bar size suitable for all rating of metering cubicle shall be 400A
POTENTIAL TRANSFORMERS:
Sr. No. | Particulars | Parameters
1 | Normal system voltage (kV r.m.s) | 11
2 | Highest system voltage (kV r.m.s) | 12
3 | Frequency | 50HZ
4 | Type | Single Phase Indoor Resin Cast
5 | Number of phases | Single phase
6 | No of PT | 3 Nos
7 | Rated Output (VA) Burden | 30VA
8 | Transformation ratio (PT ratio) | 11KV/√3/ 110V/√3
9 | Impulse withstand voltage | 75
(KV peak) (on assembled CT PT set)
10 | One minute power frequency dry withstand voltage (on assembled CT-PT set)
(a) Primary (KV rms)
| (b) Secondary (KV rms) | 28kV
3kV
11 | Class of accuracy | 0.2
12 | Rated voltage factor and time | 1.2 times continuous and 1.5 times for 30 sec
17 | System condition | Effectively earthed system
18 | Maximum temperature raise over maximum ambient temperature (which may be taken as 450C) at rated frequency and with rated Burden | Within limited of IS 16227 with latest amendment/ revision.
19 | Maximum ratio error | Within limited of IS 16227 with latest amendment/ revision.
20 | Maximum phase angle error | Within limited of IS 16227 with latest amendment/ revision.
21 | Type of Insulation
21.a | Impregnation | Class H vacuum pressure impregnation
21.b | Varnish on CT-PT windings | Class H varnish
21.c | Epoxy resin casting | Class F Resin
22 | Creepage distance | 300mm
(It is only applicable for Insulator connecting for CT, PT & Cable
Compartment, if used)
21 | Basic insulation Level | 12/28/75 KV
22 | Thickness of baseplate | 5mm, Plate shall be properly with earthing arrangement.
23 | Material of Bushings | Epoxy
24 | Material for Rod of Bushings | Copper (if applicable)